## Slide 1: Reliability improvement of gas turbine performance monitoring based on online measurement data processing
Supervisor: Prof. Ing. Alessandro Bottaro
Supervisor: Dott. Ing. Cyrille Bricaud
Candidate: Diego Fancello
Genoa, 26 Marzo 2024

## Slide 2: Ansaldo Energia Switzerland
GT36 Monitoring project:
  Accurate evaluation of gas turbine power plant performance over life time
  Monitor performance degradation to anticipate outage
Thesis target
  Reliability improvement of gas turbine performance monitoring based on online measurement data processing
  Secondary task: improve the automation of the monitoring process

## Slide 3: Chalenges of perfomance monitoring
Degradation detecting due to:
  Compressor Fouling
  Clearance change
  Seal damage
Prevent outage with regular monitoring
Identify sensor degradation leading to incorrect measurements
Distinguish performance degradation and sensor degradation
A.Massardo, Impianti per l’energia, 2021

## Slide 4: Performance evaluation
To evaluate performance, it is necessary to have:
  Measurements
  Performance monitoring tool suite
Outer heat balance:
  Input:
    Power, GT exhaust temperature, fuel massflow, fuel composition, cooling air massflow, ambient conditions
  Output:
    Compressor inlet massflow
Component performance analysis:
  Performance model it’s needed
  Input:
    Compressor discharge pressure and temperature, cooling air massflow, pressure and temperature, inlet and exhaust pressure drop, VIGV position
  Output:
    Compressor, Turbine efficiency
    Turbine Inlet temperature

## Slide 5: Performance monitoring tool
Gas Turbine model:
  Each component is characterised by variables, parameters, the equations describing its behaviour and libraries containing characteristic maps of the same;
  The model is built at the design stage and is updated over time;
Heat balance:
  Heat balances are nothing more than energy balances on control volumes;
  Use measurements and assumption as input;
  it is also necessary to integrate libraries containing the thermodynamic properties of the fluids flowing through each component.
Synthesis:
  Are calculations that provide an estimate of how the gas turbine should perform according to the characteristics of the components;
  Give a reference to compare the actual gas turbine state, ansyn factor;
Solver:
  Newton Raphson metod
  Flexibility in the choice of inputs

## Slide 6: Ansyn factor
Definined as:
  Delta:
  Ratio:
Purpose:
  Monitoring hardware degradation
  Measurements issues
Features:
  Dependent on VIGV position
  Dependent on model quality
  Indipendence form ambient conditions

## Slide 7: Why pre-processing is necessary
The measurements are affected by:
  Sensor failure
  Fouling of the sensing element
  Wrong calibration
  Performance degradation
  Presence of electromagnetic interference
  Mounting errors

## Slide 8: Automated heat balance flowchart
START
Date and Time
Stability criteria
Criteria for pre-processing of measurements for synthesis
Script extracts the measurements from Database and saves them
Folder of processed measures for synthesis calculation
Folder Raw Data
WARNING: Replaced measures
Alpeg calculations
PREDICTION
Script compare raw measurements and prediction and save the results
Folder of processed measures for Heat balances
WARNING: Replaced measures
Alpeg calculation
SMOOTHED HEAT BALANCES
Criteria for pre-processing of measurements for Heat Balance calculations
Alpeg calculations
RAW HEAT BALANCES

## Slide 9: Pre-processing criteria

## Slide 10: Pre-processing results

## Slide 11: Pre-processing results

## Slide 12: Conclusions
What’s next?
The potential of the monitoring system was demonstrated
The accuracy in detecting erroneous measurements by the processing system was demonstrated.
The effect of erroneous measurements on the results of thermal balances was demonstrated, highlighting the importance of a preprocessing system
The system allows dual monitoring of the actual state of the engine and the state of the mounted sensors.
Develop sensitivity on tollerances definition
Improve automation of the monitoring process
Early warnings in the event of serious damage

## Slide 13: Thank you for your attention
Genoa, 26 Marzo 2024